## Slide 1: Thermal Regulation through PID Control
Jake Tsuyemura
University of Hawaii at Manoa
Derek Kubo
John Kuroda
Ranjani Srinivasan
Smithsonian Submillimeter Array

## Slide 2: The Project/Motivation
Design PID Control system to regulate the temperature of sensitive equipment on the summit to within 1 °C peak-peak.
Previous temperature control system was unstable at certain temperatures
Implement this control system on any electronic enclosure
Use Arduino UNO microcontroller to implement PID and servo fanspeed
Perform Matlab Simulations using System Identification Toolbox/PID tool

## Slide 3: What is PID?
http://radhesh.files.wordpress.com/2008/05/pid.jpg
Proportional, Integral, and Derivative Control
Most common Control System
Easy to use

## Slide 4
Proportional: Kp
Current error from Setpoint Defines Proportional Term

## Slide 5
Integral: Ki
Sum of all previous errors defines Integral Term

## Slide 6
Derivative: Kd
Instantaneous rate of change defines Derivative Term

## Slide 7: Tuning Coefficients
http://www.essproducts.com/download/PIDprimer.PDF

## Slide 8
Extreme Kp, Ki, Kd Values
Collected from Full scale Model over 40 minutes
Setpoint: 40 ºC

## Slide 9: Cascaded Control
Cascade control is more complex
Primary PID loop controls setpoint of secondary PID loop
Responsive to fast/slow changes
Two sets of PID coefficients
http://www.controlguru.com/2007/090207.html

## Slide 10
Full Scale Model
48 CFM Intake Fan
48 CFM Exhaust Fan
12V, 1.5W Power Supply
20W Heater
Arduino UNO Microcontroller
Voltage Divider/ Transistor Circuitry
Near Thermistor
Far Thermistor
20W Heater

## Slide 11: Two Approaches
https://www.mathworks.com/company/events/webinars/webinarconf.html?id=30317&language=en&confirmation_page&wfsid=4690229

## Slide 12: Modeling the System
http://www.essproducts.com/download/PIDprimer.PDF
Collected open loop data of system
Matlab’s System Identification Toolbox
Selected Box Jenkins Model Representation
    Models noise with independent term
    Matlab estimates I/O delay in first term
Estimated Transfer function fit 68% against validation data

## Slide 13: Matlab PID Values
Use Matlab’s PID tool to produce coefficient values
Adjust response time to match system
Chose PI controller to simplify tuning
Derivative contained too much noise
Simulated Coefficents:
Kp: 22 Ki: .255 Kd: 0

## Slide 14
Single Loop Matlab Values
Coefficents:
Kp: 22 Ki: .255 Kd: 0
Variance: 0.01288 Peak-peak: 1.009
Setpoint: 40 ºC
AC turns off
AC turns on

## Slide 15: Large Scale Results: (Trial and Error)
Coefficients:
Primary Loop: Kp: 10 Ki: 3 Kd: .2
Secondary Loop: Kp: 70 Ki: 10 Kd: 4
Variance: 0.033 Peak-Peak: 0.905
Setpoint: 40 ºC
AC turns off

## Slide 16
Cascaded Control VS Matlab Values
Cascaded Control: Variance: 0.033 Peak-peak:.905
Matlab Values: Variance: 0.0128 Peak-peak: 1.009
Setpoint: 40 ºC
AC turns off

## Slide 17: Conclusions
It is possible to manually tune a cascaded PID to within 1 ºC peak-peak
System Identification Toolbox is capable of producing an accurate Transfer Function of a real system
Matlab’s autotune PID tool can produce reasonable PID values
Matlab values and manually tuned values had very similar performance close to or within specification

## Slide 18
Acknowledgements
Support for the 2013 Akamai Internship Program and the Akamai Workforce Initiative is provided by: the National Science Foundation (AST#0836053); Air Force Office of Scientific Research (FA9550-10-1-0044); University of Hawaii; Thirty Meter Telescope Corp.; University of California, Santa Cruz; Kamehameha Schools.
Special Thanks to:
Derek Kubo
John Kuroda
Ranjani Srinivasan

## Slide 19
Small Scale Model
Far Thermistor
Near Thermistor
20W Heater
PWM Fan
Arduino Microcontroller
Voltage Divider/Transistor Circuitry

## Slide 20: Small Scale Results: (Trial and Error)
Coefficients:
Primary Loop: Kp: 3 Ki: .3 Kd: .2
Secondary Loop: Kp: 2 Ki: .5 Kd: .2
Peak-Peak: 0.51 Variance: 0.017
Setpoint: 40 ºC
AC turns off
AC turns on

## Slide 21
Disturbance Test
Blue: Large Scale Coefficients (+-1000)
Primary Loop: Kp: 10 Ki: 3 Kd: .2
Secondary Loop: Kp: 70 Ki: 10 Kd: 4
Red: Small Scale Coefficients (0-255)
Primary Loop: Kp: 3 Ki: .3 Kd: .2
Secondary Loop: Kp: 2 Ki: .5 Kd: .2

## Slide 22
Effects of Sampling Time
Coefficients:
Primary Loop: Kp: 30 Ki: 3 Kd: .2
Secondary Loop: Kp: 70 Ki: 10 Kd: 4
Overnight Test with the same coefficents
Sampling times: 1000ms, 500ms, 200ms

## Slide 23
Comparing Big/Small Box Coefficients
Red: Big Box Values +- 1000
Primary Loop: Kp: 10 Ki: 3 Kd: .2
Secondary Loop: Kp: 70 Ki: 10 Kd: 4
Blue: Small Box Values +- 1000
Primary Loop: Kp: 3 Ki: .3 Kd: .2
Secondary Loop: Kp: 2 Ki: .5 Kd: .2
Black: Small Box Values 0-255
Primary Loop: Kp: 3 Ki: .3 Kd: .2
Secondary Loop: Kp: 2 Ki: .5 Kd: .2

## Slide 24
Open Loop Recorded Data

## Slide 25
System Identification Toolbox:
Box-Jenkins Model

## Slide 26
Best fit = 68.32%
Best-Fit Transfer Function

## Slide 27
Simulink Modeling

## Slide 28
AMIBA/SMA